## Attachment 4
Attachment 4 - Initial Options Data
Data Center Load and Cost
| Power Supply Type | Contracted |  |  | Owned
| Strategy Concept Case | A | B | C | D | E | F
| Name | Available Grid /Utility | Larger Grid / Utility | Gas Power Partner; Cost Optimized | Gas Power Self Build: Cost Optimized | Gas Power Self-Build: Scheduled Focused | Existing Coal Plant Restart
| Data Center IT Load (MW) | 200 | 480 | 1200 | 1200 | 200 | 1000
| Total Load (MW) | 300 | 600 | 1500 | 1500 | 300 | 1500
| Power Usage Effectiveness | 1.5 | 1.25 | 1.25 | 1.25 | 1.5 | 1.5
| Data Center New Land Use (Acres) | 100 | 192 | 300 | 300 | 100 | 0
| Data Center Buildings Capital Cost ($MM) | 3000 | 5760 | 9600 | 9600 | 2800 | 8000
| Racks and Processors Capital Cost* ($MM) | 1800 | 4080 | 9600 | 9600 | 1800 | 8000
| Subtotal: Data Center Capital Cost ($MM) | 4800 | 9840 | 19200 | 19200 | 4600 | 16000
| Data Center Operating Costs ($/yr) | 8000000 | 9000000 | 12000000 | 10000000 | 8000000 | 12000000
* Max 5 year useful life
Power Supply, Contracting, and Pricing
| Power Supply Type | Contracted |  |  | Owned
| Strategy Concept Case | A | B | C | D | E | F
| Name | Available Grid /Utility | Larger Grid / Utility | Gas Power Partner; Cost Optimized | Gas Power Self Build: Cost Optimized | Gas Power Self-Build: Scheduled Focused | Existing Coal Plant Restart
| Power Supply Source | Local Utility -- Existing Units | Local Utility - Planned Renewables and batteries | Islanded (no grid) Large efficient Units | Islanded (no grid) Large efficient Units | Islanded (no grid) small gas power units | Acquired Coal Plant
| Project Location | Louisiana | Louisiana | Pennsylvania | Louisiana | Louisiana | Pennsylvania
Environmental Aspects
| Power Generation New Land Use (acres) | N/A | 3350 | 100 | 100 | 100 | 0
| Air Emissions (per MWh) | High | Low/No | Medium | Medium | High | Highest
| Water Use | None | Low | Medium | Medium | Low | High
Schedule-Related
| Forecasted Operational Dates | End 2026 | End 2028 | End 2030 | End 2030 | End 2027 | End 2026
| Schedule Basis | Utility construction of interconnection | Utility Construction of Transmission and Interconnection | Equipment Lead Times | Equipment Lead Times | Permitting + Equipment Lead Times | As soon as datacenter can be built
| Initial Contract Term (yrs) | 1 | 10 | 15 | NA | NA | NA
Power Reliability
| Net Power Reliability** (%) | 100% | 99.99% | 98% | 98% | 99% | 95%
** After accounting for back-up batteries and generators
Costs
| Company Investment ($MM) | 0 | 0 | 0 | 2250 | 750 | 375
| Specific Capital Cost ($/kW) | 0 | 0 | 0 | 1500 | 2500 | 250
| Contract Demand Charges ($/yr) | 18000000 | 72000000 | 270000000 | 0 | 0 | 0
| Onsite Generation Fixed Costs** ($/yr) | 0 | 0 | 0 | 21600000 | 18000000 | 54000000
| Variable Energy Cost ($/MWh) | 35 | 60 | 3 | 3 | 7 | 5
| 2026 Base Fuel Price*** ($/MMBtu) | 0 | 0 | 3.37 | 3.87 | 3.87 | 2.5
| x Heat Rate (MMBtu/MWh) | 0 | 0 | 6.5 | 6.5 | 9.5 | 10
| = Fuel Charge ($/MWh) | 0 | 0 | 21.905 | 25.155 | 36.765 | 25
| + Variable Energy Cost ($/MWh) | 35 | 60 | 3 | 3 | 7 | 5
| = Total Variable Energy Cost ($/MWh) | 35 | 60 | 24.905 | 28.155 | 43.765 | 30
| x Max Power Demand (MWh/yr) | 2628000 | 5256000 | 13140000 | 13140000 | 2628000 | 13140000
| = Total Variable Energy Cost ($/yr) | 91980000 | 315360000 | 327251700 | 369956700 | 115014420 | 394200000
| + Fixed and Demand Charges ($/yr) | 18000000 | 72000000 | 270000000 | 21600000 | 18000000 | 54000000
| = Total Operating Costs ($/yr) | 109980000 | 387360000 | 597251700 | 391556700 | 133014420 | 448200000
*** Fuel Prices are subject to market volatility

## Attachment 5
Attachment 5 - Market Consultant Revenue Forecast
Revenue Assumptions
| Power Supply Type | Contracted |  |  | Owned
| Strategy Concept Case | A | B | C | D | E | F
| Name | Available Grid /Utility | Larger Grid / Utility | Gas Power Partner; Cost Optimized | Gas Power Self Build: Cost Optimized | Gas Power Self-Build: Scheduled Focused | Existing Coal Plant Restart
| First Year of Operations (first year of customer revenue) | 2028 | 2030 | 2032 | 2032 | 2029 | 2028
| Number of Customers in First Year | 1000000 | 800000 | 750000 | 750000 | 1000000 | 1000000
| Price Charged / User | 140 | 550 | 1500 | 1500 | 160 | 525
|  | Market Growth in Customer Acquisition |  |  | Market Solution Pricing ($/user/year)
|  | 2025 | 72% |  | Chat GTP
|  | 2026 | 72% |  | Plus | 240
|  | 2027 | 72% |  | Pro | 2400
|  | 2028 | 26%
|  | 2029 | 26.2% |  | Microsoft Copilot
|  | 2030 | 23.8% |  | Pro | 240
|  | 2031 | 20.8%
|  | 2032 | 17.8% |  | Google Gemini Code Assist
|  | 2033 | 14.8% |  | Standard | 228
|  | 2034 | 11.8% |  | Enterprise | 540
|  | 2035 | 8.8%
|  | 2036 | 5.8% |  | GitHub Copilot
|  | 2037 | 5% |  | Individual | 100
|  | 2038 | 5% |  | Organization | 228
|  | 2039 | 4%
|  | 2040 | 4% |  | Perplexity AI
|  | 2041 | 3% |  | Pro | 240
|  | 2042 | 3%
|  | 2043 | 3% |  | Character.ai
|  | 2044 | 3% |  | Plus | 120
|  | 2045 | 3%
|  | 2046 | 3% |  | Anthropic
|  | 2047 | 3% |  | Pro | 216
|  | 2048 | 3% |  | Team | 300
|  | 2049 | 3%
|  | 2050 | 3%

## Attachment 6
Attachment 6 - Illustrative example of Market Consultant revenue buildup
| Option A |  | 2028 | 2029
| Market Growth in Customer Acquisition |  | 26% | 26.2%
| Annual New Customers |  | 1000000 | 1262000
| Paid Subscribers, Beginning of Period |  | 0 | 1000000
| Less: Customer Attrition | 10% | 0 | -100000
| Retained Subscribers |  | 0 | 900000
| New Customers Acquired |  | 1000000 | 1262000
| Total Paid Subscribers |  | 1000000 | 2162000
| Price Charged / Subscriber |  | 140 | 140
| Annual Revenue |  | 140000000 | 302680000

## Attachment 7
Attachment 7 - Illustration of Reliability Value
| Power Supply Type | Contracted |  |  | Owned
| Strategy Concept Case | A | B | C | D | E | F
| Name | Available Grid /Utility | Larger Grid / Utility | Gas Power Partner; Cost Optimized | Gas Power Self Build: Cost Optimized | Gas Power Self-Build: Scheduled Focused | Existing Coal Plant Restart
| IT Load (MW) | 200 | 480 | 1200 | 1200 | 200 | 1000
| Reliability | 100% | 99.99% | 98% | 98% | 99% | 95%
| Unreliability | 0.001% | 0.01% | 2% | 2% | 1% | 5%
| x5 = Prospective Quality Loss | 0.005% | 0.05% | 10% | 10% | 5% | 25%
| kW/Rack | 40 | 40 | 40 | 40 | 40 | 40
| GPU/Rack | 4 | 4 | 4 | 4 | 4 | 4
| GPUs (#) | 20000 | 48000 | 120000 | 120000 | 20000 | 100000
| Training Duration (d) | 90 | 37.5 | 15 | 15 | 90 | 18
| Training Run Resource (GPU*d) | 1800000 | 1800000 | 1800000 | 1800000 | 1800000 | 1800000
| Example Cost Rate ($/GPU/hr) | 3.25 | 3.25 | 3.25 | 3.25 | 3.25 | 3.25
| Training Run Cost | 140400000 | 140400000 | 140400000 | 140400000 | 140400000 | 140400000
| x Prospective Quality Loss = | 0.005% | 0.05% | 10% | 10% | 5% | 25%
| Value of Quality Loss/Run | 7020 | 70200 | 14040000 | 14040000 | 7020000 | 35100000
| x Max Runs per year | 4 | 9 | 24 | 24 | 4 | 20
| = Quality Risk / Year | 28080 | 631800 | 336960000 | 336960000 | 28080000 | 702000000

## Attachment 8
Attachment 8 - Forward Gas Curves
| Calendar Year | Columbia Gulf (Louisiana) |  |  | Transco Non-New York (Pennsylvania)
|  | Forward Price Forecast | Volatility As Annual Average |  | Forward Price Forecast | Volatility As Annual Average
|  | ($/MMBtu) | Min | Max | ($/MMBtu) | Min | Max
| 2026 | 3.8746 | 94.84% | 112.9% | 3.3657 | 85.14% | 159.4%
| 2027 | 3.6098 | 94.46% | 113.9% | 3.1899 | 84.33% | 162.7%
| 2028 | 3.364 | 94.05% | 114.9% | 3.1964 | 84.36% | 162.6%
| 2029 | 3.2682 | 93.88% | 115.3% | 3.117 | 83.96% | 164.2%
| 2030 | 3.1301 | 93.61% | 116% | 2.8133 | 82.23% | 171.1%
| 2031 | 2.9852 | 93.3% | 116.7% | 2.6398 | 81.06% | 175.8%
| 2032 | 3.0133 | 93.36% | 116.6% | 2.6594 | 81.2% | 175.2%
| 2033 | 3.0129 | 93.36% | 116.6% | 2.6152 | 80.88% | 176.5%
| 2034 | 3.1205 | 93.59% | 116% | 2.7139 | 81.58% | 173.7%
| 2035 | 3.2326 | 93.81% | 115.5% | 2.8163 | 82.25% | 171%
| 2036 | 3.0257 | 93.39% | 116.5% | 2.6107 | 80.85% | 176.6%
| 2037 | 2.9343 | 93.18% | 117% | 2.5195 | 80.15% | 179.4%
| 2038 | 2.9888 | 93.31% | 116.7% | 2.5786 | 80.61% | 177.6%
| 2039 | 3.0434 | 93.43% | 116.4% | 2.6376 | 81.04% | 175.8%
| 2040 | 3.0985 | 93.55% | 116.1% | 2.702 | 81.5% | 174%
| 2041 | 3.152 | 93.65% | 115.9% | 2.754 | 81.84% | 172.6%
| 2042 | 3.2056 | 93.76% | 115.6% | 2.811 | 82.21% | 171.2%
| 2043 | 3.2591 | 93.86% | 115.3% | 2.868 | 82.57% | 169.7%
| 2044 | 3.3132 | 93.96% | 115.1% | 2.9304 | 82.94% | 168.3%
| 2045 | 3.3662 | 94.06% | 114.9% | 2.9811 | 83.23% | 167.1%
| 2046 | 3.4198 | 94.15% | 114.6% | 3.0371 | 83.54% | 165.9%
| 2047 | 3.4733 | 94.24% | 114.4% | 3.0931 | 83.83% | 164.7%
| 2048 | 3.5274 | 94.33% | 114.2% | 3.1545 | 84.15% | 163.4%
| 2049 | 3.5804 | 94.41% | 114% | 3.2051 | 84.4% | 162.4%
| 2050 | 3.634 | 94.5% | 113.8% | 3.2611 | 84.67% | 161.3%